# Specification Language: 105MTS AC21-2.0SC00 Activated Carbon Filter

## Control Valve

- The mineral tank will have one (1) 50 mm (2“), Canature WaterGroup 105 series, top mounted, plastic PPO (Noryl) body, motor driven control valve and will be of the piston/seal/spacer type.

- The valve will have an electronic controller with a 4 line display.

- The control valve will perform backwash and rapid rinse as required.

- The control valve will have an integrated turbine meter.

- The valve will be pending NSF/ANSI 44 certification for Materials and Structural Integrity Requirements.

- The control valve will be designed to work at a pressure from 137 – 862 kPa gauge (20 – 125 psig) and from temperatures of 1 °C (34 °F) to 43 °C (110 °F).

- The control valve and electronics will have a warranty of five (5) years.

## Media

- The mineral tank will contain 762 mm (30”) bed depth of high quality, NSF approved Activated Carbon.

- The mineral tank will have graded and washed quartz support bed of 76 mm (3”) gravel above the bottom of the distribution system.

## Mineral Tank

- The mineral tank will be 533 mm (21”) in diameter and 1575 mm (62”) in height.

- All mineral tanks will be NSF/ANSI 44 Certified for Materials and Structural Integrity.

- The liner material will be made of polyethylene and the outer winding will be made of a high-performance fibreglass and epoxy resin.

- The maximum operating pressure will be 1034 kPa gauge (150 psig) with an operating temperature range of 1 °C – 49 °C (34 °F – 120 °F) with a maximum vacuum of 127 mm Hg (2.46 psi).

- The system will contain one (1) mineral tank.

- The mineral tank will have a warranty of ten (10) years.

## System Set Up and Operation

- The system is set up as a calendar clock system and will have its regeneration initiated via a system timer.

- The maximum recommended operating pressure will be 139 - 689 kPa gauge (20-100 psig)

- Control valve will be connected to an electrical outlet able to supply 120V at 60Hz.

- Filtered water can be drawn continuously from the filter unit at flows of up to 14 USGPM (0.88 l/s).

- Able to perform RO pre-treat at 7 USGPM (0.4 l/s) if required.

- The backwash requirement for the filter is 24 USGPM (1.51 l/s).

## System Part Number

The filter will be a 105STS AC21-2.0SC00 as manufactured by Canature WaterGroup.