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Water Conditioner Operation Manual
Note:

1.
Read all instructions carefully before operation.

2.
Avoid pinched o-rings during installation by applying 


(provided with install kit) NSF certified lubricant to all seals.
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Figure 1. Specifications


How Your Water Conditioner Works

The principle behind water softening is simple chemistry.  A water softener contains resin beads which hold electrically charged ions.  When hard water passes through the softener, calcium and magnesium ions are attracted to the charged resin beads.  It's the resulting removal of calcium and magnesium ions that produces soft water.
This valve is controlled with simple, user-friendly electronics displayed on a large LCD screen.  The main page displays the current date and time.  In addition, the main page also shows key valve information and statistics including; current capacity setting, volume remaining, date of last regeneration, current flow rate, and peak flow rate.
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Figure 2. Main Page Displays

NOTE: 
REGEN DAYS and REMAINING DAYS are only shown in the CALENDAR CLOCK more or METER OVERRIDE mode. 
[image: image5.emf]

Figure 3. Key Pad Configuration

MENU BUTTON “
[image: image6.wmf]”:
The function of this key is to enter the level one programming mode where the valve 
settings can be adjusted.

SET / REGEN BUTTON “
[image: image7.wmf]”:
This button has two functions.  The first is to initiate a manual regeneration by holding 
the button for 3 or more seconds.  The second function is while in programming mode, 
pressing this key allows the user to change the value of each setting.

UP / DOWN “
[image: image8.wmf]
[image: image9.wmf]”:
These buttons are used to increase or decrease the value of the settings while in the 
programming mode.

System Initialization
When power is first supplied, the valve may take up to two minutes to initialize the valve.  During this time the valve will show “INTIALIZING WAIT PLEASE”.  Do not touch any buttons at this time.  When the valve reaches the service position, it will display the current date and time.
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Figure 4. System Initialization Display
Main Valve Functions
Regeneration Mode:
1.
METER DELAYED
2.
METER IMMEDIATE
 3.
CALENDAR CLOCK
4.
METER OVERRIDE

Capacity Calculation:
1.
AUTOMATIC 
2.
MANUAL 

Adjustable Cycles:
All of the valve cycles are fully adjustable.


1.
 BACKWASH
2. BRINE / RINSE
3. 
RINSE
4. 
REFILL

NOTE: 
Refer to Level Two User Programming for description of each mode.

During a regeneration cycle, the valve will display what position it is advancing to.  Once in the correct position, the valve will display the current position along with the time remaining for that cycle.  On the bottom row, the time remaining is also graphically displayed.
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 Figure 5. Regeneration Cycle Valve Display

Manual Regeneration (Delayed or Immediate)
If screen is locked, press “
[image: image12.wmf] MENU” for 3 seconds to unlock.  To initiate an immediate regeneration, press the SET / REGEN button for 3 seconds, an option for delayed or immediate regeneration will appear. Press the SET / REGEN button again and delayed will begin flashing, press the down arrow button to have immediate flash, press the SET / REGEN button and then press the menu button and the valve will immediately start into manual regeneration.
To initiate a delayed regeneration, press the SET / REGEN button for 3 seconds, then press the menu button and a regeneration will be queued to the next pre-set regeneration time (2:00 a.m.). 

Control Operation During A Power Failure 

In the event of a power failure, the valve will keep track of the time and day for 48 hours.  The programmed settings are stored in a non-volatile memory and will not be lost during a power failure.  If power fails while the unit is in regeneration, the valve will finish regeneration from the point it is at once power is restored.  However, since the unit did not complete its regeneration, it will queue another regeneration at the next scheduled regeneration time. 

If the valve misses a scheduled regeneration due to a power failure, it will queue a regeneration at the next regeneration time once power is restored.

General Installation

	Water Pressure
	Minimum 25 PSI

	Electrical Supply
	Uninterrupted AC

	Existing Plumbing
	Free of any deposits or build-ups inside pipes.

	Unit Location
	Locate close to drain and connect according to plumbing codes

	Bypass Valves
	Always provide for bypass valve if unit is not equipped with one.

	Plumbing
	Softener and or other  water treatment equipment should be installed to local plumbing codes
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	CAUTION

· Do not exceed 120 psi water pressure.

· Do not exceed 110°F water temperature.

· Do not subject unit to freezing conditions.
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Figure 6. Piping Diagram
1.
Locate the softener tank and brine tank close to a drain where the system will be installed.  The surface should be clean and level.

2.
Perform all plumbing according to local plumbing codes.

· Use a ½” minimum pipe or tubing size for the drain line

· Use a ¾” pipe or tubing for backwash flow rates that exceed 7 gpm or length that exceeds 20ft (6 m)

3.
Any solder joints near the valve must be done before connecting any piping to the valve.  Always leave at least 6" (152 mm) between the valve and joints when soldering pipes that are connected to the valve.  Failure to do this could cause damage to the valve.

4.
If the valve is not installed on the tank, cut the 1” central pipe flush with top of each tank.  Lubricate the large o-ring on the valve that seals against the tank.  Screw the valve on to the tank.  Be careful to not cross thread the valve into the tank.  Only use silicone lubricant.
5.
Connect the drain line to the valve.  Only use Teflon tape on the drain fitting.  
6. 
Connect the brine line from the brine tank to the valve.
7. 
Add water until there is approximately 1" (25 mm) of water above the grid plate.  If the tank does not have a grid, add water until it is above the air check in the brine tank.  Do not add salt to the brine tank at this time.

8. 
Place the unit in the bypass position.

9. 
Slowly turn on the main water supply.

10. 
At the nearest cold treated water tap nearby remove the faucet screen, open the faucet and let water run a few minutes or until the system is free of any air or foreign material resulting from the plumbing work.  Close the water tap when water runs clean, then proceed to start up instructions.
Start-Up Instructions

1.
Plug the valve into an approved power source.

2.
When power is supplied to the control, the screen will display “INITIALIZING WAIT PLEASE” while it finds the service position.

3.
Press “
[image: image15.wmf] SET/REGEN” and hold for 3 seconds to initiate a manual regeneration and advance the valve to the Backwash position.  Open the inlet on the bypass valve slowly and allow water to enter the unit. Allow all air to escape from the unit before turning the water on fully then allow water to run to drain for 3-4 minutes or until all media fines are washed out of the softener.
4.
Press any button to advance to the BRINE position.  Check the water level in the brine tank to insure the valve is drawing brine properly.

5.
Press any button to advance to the RINSE position.  Check the drain line flow.  Allow the water to run for 3-4 minutes or until the water is clear.

6.
Press any button to advance to the REFILL position.  Check that the valve is filling water into the brine tank. Allow the valve to refill for the correct amount of time as displayed on the screen to insure a proper brine solution for the next regeneration.

7.
 Press any button to advance to the SERVICE position. Open the outlet valve on the bypass, then open the nearest treated water faucet and allow the water to run until clear, close the tap and replace the faucet screen.
8.
Add salt into the brine tank.

9.
Program hardness and people into controller using Level One Programming Instructions.

Level I User Programming
Setting Current Time

1.
Press “
[image: image16.wmf] MENU” for 3 seconds to unlock screen.  Press “
[image: image17.wmf] MENU” again to enter level one programming mode and adjust CURRENT TIME.

2.
Press “
[image: image18.wmf] SET/REGEN” to adjust hours.  When you have entered the change value mode, the curser will blink.  Press “
[image: image19.wmf] or 
[image: image20.wmf] UP OR DOWN” arrows to change the hour values.  Press “
[image: image21.wmf] SET/REGEN” again to accept the hour value and advance to change the minutes value.  Press ““
[image: image22.wmf] or 
[image: image23.wmf] UP OR DOWN” arrows to change the minute values.  Press “
[image: image24.wmf] SET/REGEN” again to accept the minute values and advance to adjust the AM/PM values.  Press “
[image: image25.wmf] or 
[image: image26.wmf] UP OR DOWN” to change the AM/PM value.  Press “
[image: image27.wmf] SET/REGEN” again to accept the AM/PM value and exit.  When you have exited the change value mode, the curser will stop flashing.

Setting Current Date
1.
Press “
[image: image28.wmf] DOWN” to advance to CURRENT DATE.

2.
Using the same procedure as setting the time, press “
[image: image29.wmf] SET/REGEN” to enter value change mode.

Setting Number of People

1.
Press “
[image: image30.wmf] DOWN” to advance to NUMBER OF PEOPLE.

2.
Press the “
[image: image31.wmf] SET/REGEN” to change the value.  Press up or down arrows to change the values.

Setting Water Hardness

1.
Press “
[image: image32.wmf] DOWN” to advance to WATER HARDNESS.

2.
Press the “
[image: image33.wmf] SET/REGEN” to change the value.  Press “
[image: image34.wmf] or 
[image: image35.wmf] UP OR DOWN” to change the values.

Setting Vacation Mode
1.
Press “
[image: image36.wmf] DOWN” to advance to VACATION MODE.

2.
Press the “
[image: image37.wmf] SET/REGEN” to change the value.  Press “
[image: image38.wmf] or 
[image: image39.wmf] UP OR DOWN” to change the values.

Exiting Level One User Program Mode
At any time, press the “
[image: image40.wmf] MENU” to accept all changes and return to main page display.

[image: image41.emf]OPTIONS

DESCRIPTION

1 CURRENT TIME

This option is the current time of day.

2 CURRENT DATE

This option is the current date.  The date is used to track the last time the system regenerated.

3 NUMBER PEOPLE

This value is the number of people living in the home.  It is used to calculate the amount of water 

needed for daily use and the reserve capacity of the system.

4 WATER HARDNESS

This value is the maximum water hardness in grains per gallon of the raw water supply.  It is used to 

calculate the system capacity.

Yes

No

Level I User Program Mode

PARAMETER

5 VACATION MODE

This function may be activated by the user during a prolonged absence such as vacation.  The system 

will perform a brief backwash and rinse based on the advanced setting.  The purpose is to keep the 

water fresh in the softener tank and plumbing system.



Figure 7. Level I Program Options
Level I User Programming Flow Chart
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CURRENT DATE
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CURRENT DATE
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CURRENT DATE

JAN/01/2009

WATER HARDNESS

20 GPG
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4
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Figure 8. Level I User Program Flow Chart

Level II User Programming
When the Level Two Master Programming Mode is entered, all available option setting displays may be viewed and set as needed.  Depending on current option settings, some parameters cannot be viewed or set.

1.
Press “
[image: image43.wmf] MENU”for three seconds to unlock screen.

2.
Press and hold “
[image: image44.wmf]
[image: image45.wmf] UP AND DOWN” for three seconds to enter Level Two Master Programming.

[image: image46.emf]OPTIONS DESCRIPTION

ENGLISH

FRENCH

SPANISH

SOFTENER

FILTER

IRON FILTER

METER DELAYED

This is the most common setting.  When the volume remaining reaches zero gallons, the 

system will initiate a regeneration at the next  pre-set regeneration time.

METER IMMEDIATE

The unit will initiate a regeneration immediately after the volume remaining reaches zero.

CALENDAR CLOCK

The unit will initiate a regeneration at the next pre-set regeneration time  based on the 

interval of days between regeneration days.

METER OVERRIDE

When the volume remaining reaches zero gallons, the system will initiate a regeneration at 

the next  pre-set regeneration time.  If the days between regeneration is reached before the 

remaining volume reaches zero, the system will override the meter setting and initiate a 

regeneration.

4 REGENERATION TIME This setting controls the time of day when a regeneration cycle will start.

AUTOMATIC

This option automatically calculates the capacity (in gallons for meter units), refill time (in 

minutes), or regeneration day intervals (days for calendar clock mode).

MANUAL The user can manually enter values for capacity, refill time, or regeneration day intervals.

6 RESIN VOLUME

This value should be the amount of resin in cubic feet that is loaded in to the tank.  The value 

is used to calculate the system capacity and refill time.

7 SALT SETTING

This value is the salt dosage (pounds per cubic foot) to be used when regenerating the 

system.

8 REFILL FLOW RATE

This value is the flow rate(gallons per minute) of the brine line flow control (BLFC) button 

installed in the valve and is used to calculate the refill time to precisely measure the amount 

of water into the brine tank.  (Note: This value is factory preset and should not be changed 

unless the BLFC button has been changed to a different size.)

9 UNIT CAPACITY

This value (GRAINS for softeners, PPM for IRON FILTERS) is the total capacity of the system.  It 

is used to calculate the capacity of the system in gallons.

In MANUAL CAPACITY CALC. mode, the CAPACITY can be adjusted by the user.  In AUTOMATIC 

CAPACITY CALC. mode, the current calculated value is displayed but cannot be adjusted.

FORMULA CAPACITY = (UNIT CAPACITY / WATER HARDNESS) – (NUMBER PEOPLE * DAILY USAGE)

11 DAILY USAGE

This value is the average amount of water used per person per day.  It is used to calculate the 

REGEN. DAYS for calendar clocks.

12 RESERVE CAPACITY

This value is the amount of water per person in gallons to be saved for a reserve capacity.  It 

is used to calculate the CAPACITY of the system.

This value is the interval (days) between regenerations.  It is used to determine how many 

days between regenerations in the CALENDAR CLOCK mode.  It is also used as the value for 

the METER OVERRIDE mode.  It can be set by the user in MANUAL CALC. MODE.  In 

AUTOMATIC CAPACITY CALC. mode, the current calculated value is displayed but cannot be 

adjusted.

FORMULA

REGEN. DAYS = ((UNIT CAPACITY / WATER HARDNESS) / (NUMBER PEOPLE * DAILY USAGE)) - 1

14 BACKWASH

This option controls the length of time in minutes for the unit to clean the bed by reversing 

the flow of water upwards through the bed and out to the drain.

15 BRINE / RINSE

This option controls the length if time in minutes for the unit to draw regenerant (brine for 

softeners) from the second tank and slowly rinse it from the top to bottom of the tank.

16 RINSE

This option controls the length of time to give the tank a final rinse from the top to the 

bottom in order remove any last traces of the regenerant (brine) from the tank.

This option controls the length of time the brine valve will open to refill the second tank 

(brine tank for softeners) with water in order to produce the regenerate solution (brine for 

softeners) for the next regeneration cycle.  The water is accurately measured through the 

valves brine line flow control to make a precise quantity of regenerant solution.  In MANUAL 

CAPACITY CALC. mode, the REFILL time can be adjusted by the user.  In AUTOMATIC CAPACITY 

CALC. mode, the current calculated value is displayed but cannot be adjusted.

FORMULA REFILL =  SALT SETTING * RESIN VOLUME / 3 / REFILL FLOW RATE

YES

NO

VALVE OPERATION

REGEN. MODE

Level II Master Program Mode

SYSTEM LANGUAGE

3

17

13

1

5

PARAMETER

This option controls which language should be used in the valve display.

CAPACITY

RESTORE DEFAULT

REFILL

18

REGEN. DAYS

There are three basic operating modes to choose depending on the system application.

10

This option allows the current settings to be erased and changed back to the default settings.

2

CAPACITY CALC.



Figure 9. Level II Program Options

Level II User Programming Softener Flow Chart

[image: image47.emf]SYSTEM LANGUAGE
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2:00 AM
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RESIN VOLUME

1.00 FT3

RESIN VOLUME

1.00 FT3

REGEN DAYS

3 DAYS

METER CAPACITY

500 GALLONS

SALT SETTING

6 LBS/CF3

REFILL FLOWRATE

0.45 GPM

UNIT CAPACITY

99,000 GRAINS

DAILY USAGE

60 GAL/PERSON

REGEN DAYS

SALT SETTING

6 LBS/CF3

REFILL FLOWRATE  FACTOR

0.9

UNIT CAPACITY

99,000 GRAINS

RESERVE CAPACITY
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REFILL
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BACKWASH
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60 MINUTES

RAPID RINSE
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REFILL

6.0 MINUTES
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Figure 10. Level I User Program Flow Chart

Diagnostics Mode

1.
Press “
[image: image48.wmf] MENU” for three seconds to unlock screen.

2.
Press and hold the “
[image: image49.wmf] AND 
[image: image50.wmf]“ UP AND DOWN buttons for three seconds to enter Level Diagnostics Mode.


In this mode, key diagnostics can be viewed for trouble shooting and problem solving.  In addition, the values can be reset to zero individually by pressing “
[image: image51.wmf] SET/REGEN” for 3 seconds

Vacation Settings Mode

1. Press “
[image: image52.wmf]” for three seconds to unlock screen.

2. Press “
[image: image53.wmf]” to advance to VACATION MODE.

3. Press and hold the “
[image: image54.wmf] UP” for three seconds to enter the Vacation Settings Mode.  In this mode the length of time for backwash and rinse along with the frequency are set while the valve is in vacation mode.


In this mode the length of time for backwash and rinse along with the frequency are set while the valve is in vacation mode.

[image: image55.emf]PARAMETER DESCRIPTION

REGEN. DAYS

This value is the frequency of how often the unit should perform a 

brief backwash and rinse.

BACKWASH

This option controls the length of time in minutes for the unit to 

briefly clean the bed by reversing the flow of water upwards through 

the bed and out to the drain.

RINSE

This option controls the length of time to give the tank a brief rinse 

from the top to the bottom in order to remove any stale or stagnant 

water from the tank.


Figure 11. Vacation Mode Settings

System Configuration

Valve Cycle Settings


 Figure 12. Valve Cycle Settings
Injector and Drain Line Flow Control

[image: image56.emf]Tank Size (Diameter) Injector Set

Brine Line Flow 

Control (BLFC)

Drain Line Flow 

Control (DLFC)

6"

7"

8"

9" #2 (2.0 GPM)

10" #3 (2.4 GPM)

12" #4 (3.5 GPM) 

13" #6 (4.0 GPM)

14" #7 (5.0 GPM)

16" none

Suggested Softener Valve Configuration

#000 Brown

(0.70 GPM)

#1 (1.5 GPM)

#1 White

#2 Blue

#3 Yellow



Figure 13. Valve Configurations
[image: image57.emf]

Figure 14. Valve Configuration View
[image: image58.emf]
Figure 15. Bypass Installation View

Automatic Bypass
The regeneration cycle lasts approximately 2-hours, after which soft water service will be restored. During regeneration, hard water is automatically bypassed for use in the household. Hot water should be used as little as possible during this time to prevent hard water from filling the water heater. This is why automatic regeneration is set for sometime during the night and manual regenerations should be performed when little or no water will be used in the household.

Safety Float
The brine tank is equipped with a safety float which prevents your brine tank from overfilling as a result of a malfunction such as a power failure.

New Sounds
You may notice new sounds as your water softener operates. The regeneration cycle lasts approximately 2 hours. During this time, you may hear water running intermittently to the drain.

Manual Bypass
In the case of emergency, such as an overflowing brine tank, you can isolate your water softener from the water supply using the bypass valve located at the back of the control. In normal operation the bypass is open with the on/off knobs in line with the inlet and outlet pipes. To isolate the softener, simply rotate the knobs clockwise (as indicated by the word BYPASS and arrow) until they lock. You can use your water related fixtures and appliances as the water supply is bypassing the softener. However, the water you use will be hard. To resume soft water service, open bypass valve by rotating the knobs counterclockwise.
Maintenance

Adding Salt
Use only crystal water softener salt.  Check the salt level monthly.  It is important to maintain the salt level above the water level.  To add salt, simply lift the salt lid and add the salt directly into the brine tank.  Be sure the brine well cover is on and fill only to the height of the brine well.
Bridging
Humidity or wrong type of salt may create a cavity between the water and the salt. This action, known as “bridging”, prevents the brine solution from being made, leading to your water supply being hard.


If you suspect salt bridging, carefully pound on the outside of the brine tank or pour some warm water over the salt to break up the bridge.  This should always be followed up by allowing the unit to use up any remaining salt and then thoroughly cleaning out the brine tank.  Allow four hours to produce a brine solution, then manually regenerate the softener. 
Care of Your
Softener
To retain the attractive appearance of your new water softener, clean occasionally with mild soap solution.  Do not use abrasive cleaners, ammonia or solvents.  Never subject your softener to freezing or to temperatures above 120°F.
Cleaning the
Injector Assembly
Sediment, salt and silt will restrict or clog the injector.  A clean water supply and pure salt will prevent this from happening.


The injector assembly is located on the right side of the control valve.  This assembly is easy to clean.

[image: image59.emf]
Figure 16. Injector Assembly View


Shut off the water supply to your softener and reduce the pressure by opening a cold soft water faucet.  Using a screwdriver, remove the two screws holding the injector cover to the control valve body.  Carefully remove the assembly and disassemble as shown in Figure 6.  The injector orifice is removed from the valve body by carefully turning it out with a large screwdriver. Remove the injector throat the same way.  Carefully flush all parts including the screen.  Use a mild acid such as vinegar or Pro-Rust Out to clean the small holes in the orifice and throat.


Reassemble using the reverse procedure.
Resin Cleaner
An approved resin cleaner must be used on a regular basis if your water supply contains iron.  The amount of resin cleaner and frequency of use is determined by the quantity of iron in your water (consult your local representative or follow the directions on the resin package).
Valve Drive Assembly Exploded View


[image: image60.wmf]
[image: image61.emf]Item No. Part No. Part Discription Quantity

B01 05056523 BNT365 Cover 1

B02 05056136 Screw-ST3.5×13(Hexagon with Washer) 2

B03 05010045 Piston Stem Holder 1

A26 13000426 Screw-ST2.9×13(Large Wafer)   1

B04 05056139 Washer-3x13 1

B05 05010037 Screw-ST2.9×10 8

B06 05056005 Main Gear  1

B07 05030010 Bnt85 Main Pcb 1

B08 05056083 Screw-M4x14 1

B09 05056166 Screw-ST4.2×12(Large Wafer)   1

B10 05056141 Washer-4x12 1

B11 05056016 Brine Regulator 1

B12 05010023 Magnet-φ3×2.7 1

B13 05056015 Brine Gear  1

B14 05056095 Spring Detent 2

B15 05056089 Nut-M4 1

B16 05056522 Bnt365 Housing 1

B17 05056084 Screw-ST3.5x13 4

B18 05030020 Bnt85-Display(NOVO) 1

B19 05056528 Pcb Cover 1

B20 26010047 O-Ring-φ42.5×1.8 1

B21 05056527 Bnt465 Front Cover 1

B22 05056082 Screw-M3×5  2

B23 05056510 Motor-12v/2rpm 1

05030014 Motor Power Cable 1

11700005 Wire Connector 2

B24 05056045 Motor Mounting Plate 1

B25 05056501 Drive Gear 1

A04 05010081 Bnt65 Piston Rod 1

B26 05056002 Idler Gear 1

B27

05010031

Meter Assembly 1

05010046

Meter Strain Relief 1

B28

05056094

Spring Idler 1

B29 05056098 Motor Pin  1

B30 05056502 Spring Retainer 1

B31 05010029 Power Cable 1

05056013 Power Strain Relief 1

B32 05056092 Ball-1/4inch 2

B33 05056503 Magnet Holder 1

B34 05056554 Locking Knob 1

B35 05056561 Screw-ST3.5×15(CSK ) 1

B36 05056529 Bnt465 Button 4



Control Valve Assembly Exploded View


[image: image62.wmf]
[image: image63.emf]Item No. Part No. Part Discription Quantity Item No. Part No. Part Discription Quantity

A01 05056087 Screw-M5×12(Hexagon) 3 A32 05056035 BLFC Button Retainer 1

A02 05056088 Screw-M5×16(Hexagon with Washer) 2 A33 05056191 BLFC-2# 1

A03 05056047 End Plug Retainer 1 A34 05056138 O-Ring-φ14×1.8  1

A04 05010081 Bnt65 Piston Rod 1 A35 05056100B BLFC Fitting 1

A05 05056097 Piston Pin 1 A36 05056106 Brine Line Screen 1

A06 05056023 End Plug 1 A37 05056107 BLFC Tube Insert 1

A07 05056070 Quad Ring 2 A38 05056033 BLFC Ferrule 1

A08 05056024 End Plug Washer 1 A39 05056108 BLFC Fitting Nut 1

A09 05056022 Piston Retainer 1 A40 05056086 Screw-M5×30(Hexagon with Washer)  2

A10 05056181 Piston (Electrical) 1 A41 05056029 Injector Cover 1

A11 05056104 Muffler 1 A42 05056072 O-Ring-φ24×2

A12 05056021 Spacer 4 A43 05056103 Injector Screen 1

A13 05056073 Seal 5 A44 05056027 Injector Nozzle 1

A14 05056019 Bnt65 Valve Body 1 A45 05056028 Injctor Throat 1

A15 05056063 O-ring-φ78.74×5.33 1 A46 05056177 Injector Body 1

A16 05056129 O-ring-φ23×3 4 A47 05056075 Injector Seat 1

A17 05056025 Adaptor Coupling 2 A48 05056134 O-Ring-φ12×2 1

A18 05056044 Adaptor Clip 2 A49 05056054 Injector Stem 1

A19 05056090 Screw-ST4.2×13(Hexagon with Washer) 2 A50 05056031 Injector Spacer 1

A20 21709003 Secure Clip 2 A51 05056081 O-Ring-φ12.5×1.8 1

A21 05056140 Valve Connector 1 A52 05056030 Injector Cap 1

A22 05056065 O-ring-φ23.6×2.65 2 A53 05056093 Injector Screen 1

A23 21319006 Screw Adaptor 2 A54 05010049 Special Washer 1

A24 26010103 O-ring-φ25×3.55  1 A55 05056105 Retaining Ring 1

A25 07060007 Valve Bottom Connector 1 A56 05056067 O-Ring-φ7.8×1.9)  2

A26 13000426 Screw-ST2.9×13(Large Wafer)   2 A57 05056037 Air Disperser 1

A27 05056038 Drain Fitting 1 A58 05056066 O-Ring-φ11×2 1

A28 26010003 O-Ring-φ18×2.65 1 A59 05056055 BLFC Plug 1

A29 05056036 DLFC Button Retainer 1 A60 05056156 Injector Nozzle(Filter) 1

A30 05056079 O-Ring-φ15×0.8 1 A61 05056117 Injector Plug 1

A31 05056143 DLFC-2# 1


Trouble Shooting
[image: image64.emf]Issue Possible Cause Possible Solution

1. No power supply. Check electrical service, fuse, etc.

2. Defective circuit board. Replace faulty parts.

3. Power failure. Reset time of day.

1. By-pass valve open. Close by-pass valve.

2. Out of salt. Add salt to tank.

3. Plugged injector / screen. Clean parts.

4. Flow of water blocked to brine tank. Check brine tank refill rate.

5. Hard water in hot water tank. Repeat flushing of hot water tank required.

6. Leak between valve and central tube. Check if central tube is cracked or o-ring is 

damaged.  Replace faulty parts.

7. Internal valve leak. Replace valve seals, spacer, and piston assembly.

C. Salt use is high. 1. Refill time is too high. Check refill time setting.

1. Iron or scale build up in line feeding unit. Clean pipes.

2. Iron build up inside valve or tank. Clean control and add resin cleaner to clean bed.  

Increase regeneration frequency.

3. Inlet of control plugged due to foreign materal. Remove piston and clean control valve.

1. Air in water system. Check well system for proper air eliminator 

control.

2. Incorrect drain line flow control (DLFC) button. Check for proper flow rate.

1. Plugged injector or screen. Clean parts.

2. Valve not regeneratiing. Replace circuit board, motor, or control.

3. Foreign material in brine valve. Clean parts.

1. Drain line flow control is plugged. Clean parts.

2. Injector or screen is plugged. Clean parts.

3. Inlet pressure too low. Increase pressure to 25 PSI.

4. Internal valve leak. Replace seals, spacers, and piston assembly.

H. Valve continuously cycles. 1. Defective position sensor PCB. Replace faulty parts.

1. Valve settings incorrect. Check valve settings.

2. Foreign material in control valve. Clean control.

3. Internal leak. Replace seals, spacers, and piston assembly.

A. Unit fails to initiate a 

regeneration cycle.

B. Water is hard.

D. Low water pressure.

E. Resin in drain line.

F. Too much water in brine 

tank.

I. Flow to drain continuously.

G. Unit fails to draw brine.


[image: image65.png]Brine Tank with Feeder Assembly Instructions

Step 1
Install salt plate and align brine well opening with the tank handle.

Step 2
Install feeder bracket into the 2 pre-drilled holes.

Step 3
Install brine well. Feed W|ck from feeder into the openingin the brine
well cap.

Step 4 -
Push feeder into brine well cap as sho n to complete the assembly.





NovoSoft Guarantee
Novo Water Conditioning Products guarantees that your new water conditioner is built of quality material and workmanship.  When properly installed and maintained, it will give years of trouble free service.

Seven Year Complete Parts Guarantee

Novo Water Conditioning Products will replace any part which fails within 84 months from date of manufacture, as indicated by the serial number, provided the failure is due to a defect in material or workmanship.  The only exception shall be when proof of purchase or installation is provided and then the warranty period shall be from the date thereof.

Life Time Year Guarantee on Mineral Tanks and Brine Tanks

Novo Water Conditioning Products will provide a replacement mineral tank or brine tank to any original equipment purchaser in possession of a tank that fails provided that the water conditioner is at all times operated in accordance with specifications and not subject to freezing.

General Provisions

Novo Water Conditioning Products assumes no responsibility for consequential damage, labour or expense incurred as a result of a defect or for failure to meet the terms of these guarantees because of circumstances beyond its control.
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Item # 





Model  





Capacity Grains 





Flow Rate 





Mineral tank size  inches











Resin Cu. Ft. 





Brine Tank /Cabinet Size inches 

















Salt Cap Lbs 





Shipping  weight lbs 











At the stated service flow rates, the pressure drop through these devices will not exceed 15 psig.


Changing salt settings from factory setting may require changing injector sizes to achieve stated capacities


The manufacturer reserves the right to make product improvements which may deviate from the specifications and descriptions stated herein, without obligation to change previously manufactured products or to note the change.





C indicates cabinet Models


Maximum Water Temperature = 110°F (43°C)


Maximum Operating Pressure = 100 PSIG (689 kPa)


Voltage = 110 volts standard


Pipe Size = 3/4”





CONTACT YOUR REGIONAL SALES MANAGER 
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